LOT 1

TECHNICAL SPECIFICATION NO 1

NAME: PHOTOVOLTAIC PANELS

QUANTITY: 28896±0,8% (depending on nominal power)

MODEL/YEAR OF MANUFACTURE: BIFACIAL/2021-2022

MANUFACTURER/COUNTRY:

| MINIMUM TECHNICAL CHARACTERISTICS | YES | NO | OBSERVATIONS |
| --- | --- | --- | --- |
| GENERAL PARAMETERS OF THE EQUIPMENT |  |  |  |
| Nominal power panel: 665Wp±0.8% Nominal power power plant: 19.215MWp |  |  |  |
| Quantity: 28896±0,8% (depending on nominal power) |  |  |  |
| Panel type: Bifacial |  |  |  |
| Bifacial gain: minimum 0.7 |  |  |  |
| Cell type: Si-monocrystalline (c-Si), 132 |  |  |  |
| Module Dimensions: Length: maximum 2.400 m Width: maximum 1.310 m Thickness: 30...35mm |  |  |  |
| Weight: maximum 40 kg |  |  |  |
| Efficiency: minimum 21% |  |  |  |
| Power Selection: positive, +5W |  |  |  |
| Maximum System Voltage: 1500V |  |  |  |
| Maximum Power Point Voltage VMPP (V): >=38 |  |  |  |
| Maximum Power Point Current IMPP (A): >=17 |  |  |  |
| Open Circuit Voltage-VOC (V): >=45 |  |  |  |
| Short Circuit Current- ISC (A): >=18 |  |  |  |
| Degradation: Maximum 2% first year degradation Maximum 0.45% Annual Power degradation |  |  |  |
| Operational Temperature: -40ºC...+85ºC |  |  |  |
| Warranty: Minimum 12 years construction warranty Minimum 30 years power warranty |  |  |  |
| ACCESSORIES |  |  |  |
| Cables: Photovoltaic Technology Cable PV1-F: 4.0mmp or 6.0mmp Portrait: 280-350mm on each polarity Length can be customized |  |  |  |
| Connector: standard MC4 |  |  |  |
| OTHER REQUIREMENTS |  |  |  |
| Documents to be provided by the contractor when contracting the products: i. Declarations of conformity ii. Warranty certificate iii. Operation and maintenance manuals iv. List of delivered components v. Panel flash report vi. Electroluminescence ratio (optional) All operating training materials and manuals shall be written in Romanian or English and shall contain all information necessary for the operation and maintenance of the equipment by the beneficiary's authorized personnel. |  |  |  |
| CERTIFICATION |  |  |  |
| The equipment must comply with all the legal conditions for placing on the market in Romania by presenting the European (CE Mark) certificate and or the manufacturer's Declaration of Conformity with Directives IEC61215, IEC61730, IEC61701, IEC62716 or equivalent directives. |  |  |  |
| WARRANTY AND POST WARRANTY |  |  |  |
| Minimum 12 years from the date of signature of the equipment acceptance certificate. |  |  |  |
| ASSOCIATED SERVICES INCLUDED |  |  |  |
| Transport will be included in the final price of the equipment |  |  |  |
| Number of panels per container: 500-600 pieces Number of panels per pallet: 25-30 pieces |  |  |  |
| Sorting in 3 power classes |  |  |  |