LOT 2

TECHNICAL SPECIFICATION NO. 2

NAME: CENTRAL INVERTER- MEDIUM VOLTAGE POWER STATION

QUANTITY: 4

MODEL/YEAR OF MANUFACTURE:

MANUFACTURER/COUNTRY:

| MINIMUM TECHNICAL CHARACTERISTICS | YES | NO | OBSERVATIONS |
| --- | --- | --- | --- |
| 1. INVERTER |  |  |  |
| GENERAL EQUIPMENT PARAMETERS |  |  |  |
| Inverter type: Central Inverter |  |  |  |
| Inverter and transformer equipment in the same enclosure |  |  |  |
| Encapsulation: equipped metal structure/skid |  |  |  |
| INVERTER INPUT (C.C) |  |  |  |
| Maximum DC current: 4500-4800A |  |  |  |
| Number of DC inputs: 24 double pole fused |  |  |  |
| Maximum DC voltage (V): 1500 |  |  |  |
| Available fuses (per input): 200A, 250A, 315A, 350A, 400A, 450A, 500A |  |  |  |
| Maximum Power Point voltage range (V):1000...1350 |  |  |  |
| Number of MPPT: minimum 1 |  |  |  |
| Efficiency: >98.5% |  |  |  |
| INVERTER OUTPUT (AC) |  |  |  |
| Nominal power from -25° ... +35°/40° (kVA): 4600/4140 |  |  |  |
| Nominal AC current from 35 to 50°C (A): 3400...3800 |  |  |  |
| Nominal output voltage AC inverter: >0.60 |  |  |  |
| Rated AC output voltage of transformer (kV): 20 |  |  |  |
| AC power frequency / range (Hz): 50/ 47 to 53 |  |  |  |
| Maximum harmonic distortion: <3% |  |  |  |
| Power factor at rated power/displacement power factor adjustable: 0.8 - 1.0 |  |  |  |
| INVERTER PROTECTION DEVICES |  |  |  |
| Input-side disconnection point - DC load break switch |  |  |  |
| Output-side disconnection point - AC circuit breaker |  |  |  |
| DC overvoltage protection - type I and II |  |  |  |
| AC overvoltage protection - class I and II |  |  |  |
| Degree of protection: electronics/ventilation and connection area: IP54/IP34/IP34 |  |  |  |
| GENERAL CHARACTERISTICS CENTRAL INVERTER |  |  |  |
| Dimensions W/H/D (mm): 2800-2850 / 2300-2350 / 1500-1600 |  |  |  |
| Weight: <4000kg |  |  |  |
| Self-consumption, average (W): <2000 |  |  |  |
| Operating temperature range: -25°C ...60°C |  |  |  |
| Possibility to extend storage batteries |  |  |  |
| 18 double pole fused (36 single pole fused) for PV and 6 double pole fused for batteries |  |  |  |
| CERTIFICATION: |  |  |  |
| CE, IEC / EN 62109-1, IEC / EN 62109-2 EMC certification: IEC 55011, IEC 61000-6-2, FCC Part 15 Class A or equivalent |  |  |  |
| GENERAL STATION/SKID CHARACTERISTICS |  |  |  |
| Dimension W/H/D (mm): max 6100/2900/2450 |  |  |  |
| Volmetry: 20-ft. container |  |  |  |
| Weight (t): maximum 18.5 |  |  |  |
| Averaging cells: included |  |  |  |
| Transformer cell: Yes |  |  |  |
| Connection cell/line: Yes |  |  |  |
| Protection: medium-voltage circuit breaker with vacuum quenching chamber rated at 24kV installed in transformer cell |  |  |  |
| Degree of protection according to IEC 60529 - Control chambers IP23D, inverter electronics IP54 or equivalent. |  |  |  |
| Degree of protection according to IEC 60721-3-4-4C1, 4S2 or equivalent. |  |  |  |
| Maximum permissible value for relative humidity (%): 95% (for 2 months/year) |  |  |  |
| Maximum operating altitude above MSL (m): 1000 |  |  |  |
| Auxiliary service transformer, power (kVA): up to 40 |  |  |  |
| Certifications: IEC 60076, IEC 62271-200, IEC 62271-202, EN50588-1 or equivalent. |  |  |  |
| 2.TRANSFORMER |  |  |  |
| GENERAL EQUIPMENT PARAMETERS |  |  |  |
| Nominal AC power 35 °C /50 °C (kVA): 4600/4140 |  |  |  |
| Transformer ratio (kV/kV) 20/ AC voltage inverter |  |  |  |
| Voltage regulation steps (%): ±2 x 2.5 |  |  |  |
| Frequency (Hz): 50 |  |  |  |
| Transformer connection type: Dy5...Dy11 |  |  |  |
| No-load losses (kW): <4.5 |  |  |  |
| Short circuit losses at 75 °C (kW): <40 |  |  |  |
| Maximum Efficiency Index (PEI) according to EN 50588-1 (%) 99.534 or equivalent |  |  |  |
| Impedance voltage at rated current at 75 °C (%): 6-8.5 |  |  |  |
| Maximum equipment voltage Um (kV) 24 |  |  |  |
| Transformer cooling medium: KNAN |  |  |  |
| Maximum altitude above sea level (m): 4000 |  |  |  |
| Ambient temperatute (min. / max.) (°C): -25...50 |  |  |  |
| Manufacturers regulation: IEC 60076 or equivalent |  |  |  |
| Total weight (kg): <9000 |  |  |  |
| Oil weight (kg): <2000 |  |  |  |
| Oil type: ester based |  |  |  |
| Protective coating according to ISO 12944-5; C-3H or equivalent |  |  |  |
| Degree of Protection according to IEC 60529; IP23 or equivalent |  |  |  |
| Transformer protection - Resistance thermometer PT100 for analogue oil temperature measurement |  |  |  |
| ACCESSORIES REQUIRED FOR THE STATION |  |  |  |
| -Oil filling pipe -Oil sampling valve -Lifting equipment -Earthing terminals -Nameplate -Warnings -Keys -Documentation |  |  |  |
| OTHER REQUIREMENTS |  |  |  |
| Documents needs to be submitted by the provider upon delivery of the products: i. Declaration of conformity ii. Warranty certificate iii. Installation, operation (operation and adjustment) and maintenance manuals / repair technology and spare parts list iv. List of delivered components v. Inverter test reports vi. Transformer test reports vii. Test reports on medium voltage cells viii. Consumable components ix. List of monitoring addresses on MODBUS protocol All training materials and manuals shall be written in Romanian or English and shall contain all information necessary for the operation and maintenance of the equipment by the beneficiary's authorised employee. |  |  |  |
| CERTIFICATION |  |  |  |
| The equipment must meet all legal conditions for placing on the market in Romania by presenting the European CE Mark certificate and or the manufacturer's Declaration of Conformity with: CE, IEC or equivalent/ EN 62109-1, IEC or equivalent/ EN 62109-2 or equivalent for inverter IEC 60076 or equivalent, IEC 62271-200 or equivalent, IEC 62271-202 or equivalent, EN50588-1 or equivalent for station |  |  |  |
| WARRANTY AND POST WARRANTY |  |  |  |
| Warranty period: minimum 60 months from the date of signature of the Equipment Acceptance Certificate. Possibility of warranty extension Maximum time for a service intervention to be 48 hours maximum from communication. |  |  |  |
| ASSOCIATED SERVICES INCLUDED |  |  |  |
| Transport need to be made to the beneficiary, at the delivery location indicated by the beneficiary. These operations will be included in the final price of the equipment. |  |  |  |
| DDP transport |  |  |  |