LOT 3

TECHNICAL SPECIFICATION NO. 3

NAME: MEDIUM VOLTAGE CABLES

QUANTITY: F4-List with the quantities of tools and technological equipment, including endowments

MODEL/YEAR OF MANUFACTURE: 2022-2023

MANUFACTURER/COUNTRY:

| MINIMUM TECHNICAL CHARACTERISTICS | YES | NO | OBSERVATIONS |
| --- | --- | --- | --- |
| CABLE NA2XS(FL)2Y 3x(1x150/25 mmp) |  |  |  |
| Rated voltage: 12/20kV |  |  |  |
| Maximum system voltage: 24kV |  |  |  |
| AC test voltage (5 min.): 42kV |  |  |  |
| Maximum rated conductor temperature: - normal conditions: 90°C - over-temperature conditions: 130°C - short circuit (maximum duration 5s): 250°C |  |  |  |
| Instalation temperature: minimum -20°C |  |  |  |
| ambient temperature during operation: -30°C ÷ 50°C |  |  |  |
| Conductor: compacted AL |  |  |  |
| semiconductor layer: extruded elastomer layer |  |  |  |
| screen section: 25 mm2 |  |  |  |
| Insulation: XLPE low density |  |  |  |
| outer cover: PVC or PE |  |  |  |
| Max. load when underground twisted 3 pole cable 150mmp conductor:>340A |  |  |  |
| Max. load when underground twisted 3 pole cable 240mmp conductor: >440A |  |  |  |
| Max. permissible Short Circuit current for 1s in conductor: 25kA |  |  |  |
| Maximum allowable short-circuit current for 1s in screen: 5.1kA |  |  |  |
| Longitudinal water blocking sheath- preferable Longitudinal water blocking cable- preferable |  |  |  |
| OTHER REQUIREMENTS |  |  |  |
| Documents to be provided by the contractor upon delivery of the products: i. Declaration of conformity ii. Warranty certificate iii. List of delivered products iv. Factory test report All training materials and manuals shall be written in Romanian or English and shall contain all information necessary for the operation and maintenance of the equipment by the beneficiary's authorised personnel. |  |  |  |
| CERTIFICATION |  |  |  |
| The equipment must meet all legal conditions for placing on the market in Romania by presenting the European CE Mark certificate and or Manufacturer's Declaration of Conformity with: DIN VDE 0276-620, HD 620 S2, IEC 60502 or equivalent |  |  |  |
| WARRANTY AND POST WARRANTY |  |  |  |
| Warranty period: minimum 24 months from the date of signing of the equipment acceptance report. |  |  |  |
| ASSOCIATED SERVICES INCLUDED |  |  |  |
| Transport will be included, to the delivery location indicated by the beneficiary. |  |  |  |